## Slide 1: Power flow calculations – Practical session
Hakan Ergun 24 February 2025
KU Leuven – Etch / EnergyVille

## Slide 2: Quick - check
Was everybody able to install software and run the code?
Any other issues, or questions so far?

## Slide 3: Let us play play with the single cable example
220 kV UGC:
We can calculate the current flow using the total impedance of the system
  Ztot = (-jXc) // R+jXl + (-jXc // Zl)
  Ul = 222.2 kV
  Sl = 30.6 MVA
G
Zl = 1613.3 Ohm (30 MVA @220 kV), purely resistive
50 km
Zl
Ul

## Slide 4: How does the voltage profile change, if the length increases?
Can you easily analyse this in the code?

## Slide 5: Comparison with last session

## Slide 6: How can we see how much reactive power the cable requires from the results?
We first need to tweak our code a bit: Let’s look at a cable length of 100 km.
After solving the problem for 100 km, you can print the results as follows:
  result = PowerModels.compute_ac_pf(data) #solve the problem
  PowerModels.update_data!(data, result["solution"]) # write solution into data
  flows = calc_branch_flow_ac(data) # calculate power flows
  PowerModels.update_data!(data, flows) # write flows into data
  The flows can be found under:
    data[“branch”][“1”][“pf”]
    data[“branch”][“1”][“pt”]
    data[“branch”][“1”][“qf”]
    data[“branch”][“1”][“qt”]
What are the losses in the system?
How much reactive power is needed by the cable?

## Slide 7: Solution
Losses: Power flowing in the “from” direction + power flowing in the “to” direction give you the losses
  Active power flow 1 -> 2: 30.800038060792765 MW
  Active power flow 2 -> 1: -30.000000006189744 MW
  Losses = 0.8 MW
Similarly, the reactive power demand is qf+qt
  Rective power flow 1 -> 2: -358.1548007648668 Mvar
  Rective power flow 2 -> 1: 4.9039280969331855e-8 Mvar
Is the result realistic?

## Slide 8: From last time…..

## Slide 9: We also see that the reactive power needs to be all absorbed by the generator…
Table: bus
vm, va
1: 1.000, 0.000
2: 1.041, -0.011
Table: gen
pg, qg
1: 0.308, -3.582
… note this is in pu of 100 MVA -> 358.2 Mvar

## Slide 10: Let’s compensate
Can you add two shunt inductances (on both sides) to compensate?
  What will the reactance be in Ohm & pu
To include shunts, you can amend
  data["shunt"]["1"] = Dict() # create dictionary
  data[“shunt”][“1”][“shunt_bus”]= … # to which bus is it connected
  data[“shunt”][“1”][“status”]= 1 # 1 is on, 0 is off
  data[“shunt”][“1”][“gs”]= …. # shunt conductance in pu
  data[“shunt”][“1”][“bs”]= …. # shunt admittance in pu
  data[“shunt”][“1”][“index”]= 1 # index for internal book keeping, can be same as element number of dictionary

## Slide 11: Calculating the value for the reactances
reactive_flow = data["branch"]["1"]["qf"] * data["baseMVA"] + data["branch"]["1"]["qt"] * data["baseMVA"]
q_comp = reactive_flow * 1e6 / 2 # divide by half because of double sided compensation
x_comp =(u_1^2 / q_comp) / zbase # calculate reactance value in pu
b_comp = 1 / x_comp # convert to shunt admittance
result = PowerModels.compute_ac_pf(data)
PowerModels.print_summary(result["solution"])
Table: bus
vm, va
1: 1.000, 0.000
2: 0.998, -0.007
Table: gen
pg, qg
1: 0.300, 0.071

## Slide 12: Let’s go meshed!!!
We will use the IEEE 30 bus network (case30.m, pf_meshed_grid.jl)

## Slide 13: Let’s inspect the data and results
Generator 1 and 2 absorbing reactive power
Can we say which elements are inductive and which ones inductive/ capacitive?

## Slide 14: Inspecting the data and results
The branches on the lower voltage levels are purely inductive.
Branches on 132 kV level are also capacitive.

## Slide 15: Let’s try three compensation options
Branch 2 going from bus 1 to bus 3
  Option 1: On one side
  Option 2: On both sides
  Option 3: Midpoint
Bc = 0.408 pu

## Slide 16: Comparing the options
Base case
Option 1a: Bus 1
Option 1b: Bus 3
Option 2:
Option 3:
WHAT DO YOU OBSERVE?